## Slide 1: The Digitalization of Fire Systems in Industry 4.0
Dr. Rodger Reiswig, SET, PMSFPE
Automatic Fire Alarm Association (AFAA)

## Slide 2: Data Centers Things to Consider

## Slide 3: Learning Objectives & Outcomes
What makes Data Centers different?
What do you think is done today, and likely to happen tomorrow?
How do we design to meet those challenges and the critical nature requirement?
What can you share as from your own perspectives?

## Slide 4: What makes Data Centers (DCs) different
A DC has many ‘standard rooms’ i.e. Power, UPS, etc is no different.
The “White Space” – the data halls themselves – are very different, and evolving rapidly.
High speed cooling, to keep processors safe, means fires will lack the usual heat:smoke development.
For instance:
Smoke will lack thermal buoyance;
Smoke will also disperse, rapidly;
Free cooling (not recirculation) means smoke levels will not accumulate; smoke is displaced;
So what?

## Slide 5: Fire, Life Safety & Business Continuity Objectives
Will the facility be occupied by people?
Will there be:
            Large quantities of Lithium-Ion batteries in use?
          Robots?
          Storage movers?
          Secondary power supplies?
Are there redundant facilities that can take over in the event of a major fire?
Will equipment be shut down when a fire is detected?
If automatic protection, does that cause abrupt power removal; is graceful shutdown remotely triggered or on a timer; is their EPO buttons for Fire Department use … who does what and when?

## Slide 6: What Codes and Standards are being applied?
NFPA 72 National Fire Alarm and Signaling Code
NFPA 75 Standard for the Fire Protection of Information Technology Equipment
NFPA 76 Standard for the Fire Protection of Telecommunications Facilities
NFPA 101 Life Safety Code
ICC Series, IBC, IFC, etc.

## Slide 7
NFPA 72, 2025
Chapter 17 – Initiating devices
17.7.4.2.3.1* In the absence of specific performance-based design criteria, detectors on ceilings up to 40 ft (12.2 m) in height shall be spaced in accordance with either of the following:
(1) The detectors shall comply with the following:
  (a) The distance between detectors shall not exceed a nominal spacing of 30 ft (9.1 m).
  (b) There shall be detectors within a distance of one-half the nominal spacing, measured at right angles from all walls or partitions extending upward to within the top 15 percent of the ceiling height.
(2)* All points on the ceiling shall have a detector within a distance equal to or less than 0.7 times the nominal 30 ft (9.1 m) spacing (0.7S).

## Slide 8
NFPA 72, 2025
Chapter 17 – Initiating devices
17.11 Acoustic Leak Detection.
17.11.1 General.
17.11.1.1
The design documentation for an acoustic leak detector shall state the required performance objective of the system.
17.11.1.2
The purpose and scope of Section 17.11 shall be to provide requirements for the selection, location, and spacing of acoustic leak detectors.

## Slide 9
Chapter 17 – Initiating devices
17.12 Thermal Image Fire Detection.
17.12.1 Thermal image fire detection systems and all the components thereof, including hardware and software, shall be listed for the purpose of fire detection.
17.12.2 Thermal image fire detection systems shall comply with the applicable requirements of Chapters 1, 10, 11, 14, 17, and 23.
17.12.2.1 Systems shall be designed in accordance with the performance-based requirements of Section 17.3.
17.12.2.2 The location and spacing of thermal image fire detectors shall comply with the requirements of 17.13.5.
17.12.2.3 A thermal image fire detector shall have clear line-of-sight to the hazard it is protecting.

## Slide 10
NFPA 72
Notes: [Brad] – Thank you Terry. Next Rodger Reiswig will discuss observations from the data analysis and how they could be applied to requirements in NFPA 72. Rodger, gives us your opinion on how the data analysis could help the NFPA 72 technical committee.
[Rodger]

## Slide 11
NFPA 72, 2025
National Fire Alarm and Signaling Code
14.1.1 The inspection, testing, and maintenance of systems, their initiating devices, and notification appliances shall comply with the requirements of this chapter.
14.1.4 The requirements of this chapter shall apply to both new and existing systems.
Notes: [Rodger]

## Slide 12
NFPA 72, 2025
National Fire Alarm and Signaling Code
14.2.1 Purpose.
14.2.1.1* The purpose for initial and reacceptance inspections shall be to ensure compliance with approved design documents and to ensure installation in accordance with this Code and other required installation standards.
NFPA 72 PURPOSE
Notes: [Rodger]

## Slide 13
Some items that we are observing with Data Centers
Perspectives:
Manufacturer
Installer
Maintainer

## Slide 14
Think fire:
Smoke and heat development
Not just IT hardware, but also IT cabling and infrastructure
False alarm phenomena
Cold aisles use a raised floor as a supply plenum

## Slide 15
Think fire:
Smoke and heat development
Not just IT hardware, but also IT cabling and infrastructure
False alarm phenomena
Hot aisles do not need a raised floor

## Slide 16: What about NFPA … 75 (FM DS 5-32 uses 5f/s ~ 1.5m/s ~ 60 ACH)

## Slide 17: Life Safety Systems – Challenges in Storage Occupancies, Building Size and Political Pressure….
Installation of plenum wire across trusses, beams, etc.
Causing service issues over time
Seismic activity as well as regular building operations shifting buildings

## Slide 18
Horns vs. speakers for notification
Prepares the owner for basic Mass Notification Systems abilities
  Building codes requiring risk analysis for Mass Notification Systems
Owners want lowest cost option
More building codes driving for speakers

## Slide 19
Newer LED strobes offering higher candela, 185 cd and more
AHJs allowing for high output strobes over audible

## Slide 20
Robotic machines and lithium-ion batteries

## Slide 21: Fire detection is an integral part of a robust strategy (Emergency Response Plan)

## Slide 22
NFPA 76 — Standard for the Fire Protection of Telecommunications Facilities (2024)
A.6.5.1
The depowering procedure often includes special marking of otherwise standard power disconnect equipment. The depowering procedure is permitted to be progressive, depending upon the severity of the incident, from circuit pack to equipment bay to area of a central office (see Figure A.‍6.5.1).
Notes: “Emergency Response Plan” – ERP agreed with AHJ (per NFPA and ICC)

## Slide 23
Contact —— .
DR. Rodger Reiswig, SET, PMSFPE
Fellow & VP, Industry Relations
Email: Rodger.Reiswig@jci.com
Phone: 321-689-0798
Web: JohnsonControls.com
AFAA.org