## Slide 1: Protection of Lithium-ion Battery Manufacturing & Storage
James Lake, IFSA

## Slide 2: Learning Outcomes.
Discuss the hazards presented by Lithium-ion battery manufacturing and storage.
Navigate the current published protection guidance.
Identify the fire sprinklers that are approved to provide protection

## Slide 3: Learning Outcomes.
Discuss the hazards presented by Lithium-ion battery manufacturing and storage.
Navigate the current published protection guidance.
Identify the fire sprinklers that are approved to provide protection

## Slide 4: State of Charge
The real-time amount of energy stored in a system, compared to the rated capacity. Stated as a percentage.
  Most finished products in storage – 40%-60%
  DOT transportation limits – 30%
  In-use or charging – 100%+

## Slide 5: Thermal Runaway

## Slide 6: Thermal Runaway
Pressurized combustible electrolyte in cell
Damage to cell caused by:
  Thermal Abuse
  Electrical Abuse
  Mechanical Abuse
  Internal Short Circuit
Cascading Thermal Runaway

## Slide 7: Protection Guidance
Table A.20.4(a) Items outside the Scope of NFPA 13 Batteries
- Lithium and other similar exotic metals
- Lithium-ion and other rechargeable batteries that contain combustible electrolyte

## Slide 8: Protection Guidance

## Slide 9: FMDS 8-1 Commodity Classifications

## Slide 10: FMDS 7-112 Protection
General Requirements
Formation & Aging Areas
          Open-Frame Rack Arrangements
          In-Rack Sprinkler Location & Design
          Bin-box or Enclosed Chamber Arrangements
Finished Cell/Modules/Batteries – Incidental Storage
Cells/Modules/Batteries in Finished Products – Storage
Storage
ASRS Storage

## Slide 11: General Requirements
Manufacturing Areas
        Per Hazards Present
Cell/Electrode Assembly
  HC3
Formation and Aging
  Section 2.4.2
Installation Guidance
  FMDS 2-0

## Slide 12: Manufacturing Areas – FMDS 3-26
K5.6 K8.0 K11.2 K14.0* K16.8*
*Approved storage sprinklers are also FM Approved for use as non-storage sprinklers.

## Slide 13: Formation & Aging Areas

## Slide 14: In-Rack Sprinkler Layout – Single Row Rack

## Slide 15
In-Rack Sprinkler Layout – Double Row Rack

## Slide 16
In-Rack Sprinkler Layout – Bin Box

## Slide 17: FM Approved In-Rack Sprinklers for FMDS 7-112
K-8.0
K-11.2
K-8.0
K-8.0

## Slide 18: Incidental Storage
Cells/modules/batteries are stored in metal or cardboard boxes.
Storage area is limited to no more than 200 ft2
Storage height is limited to 6 ft.
Multiple storage areas are separated by aisles not less than 10 ft wide.
Battery state of charge is less than or equal to 60%.

## Slide 19: Incidental Storage
Cells/modules/batteries are stored in unexpanded plastic containers.
Storage area is limited to no more than 200 ft2
Storage height is limited to 6 ft.
Multiple storage areas are separated by aisles not less than 10 ft wide.
Battery state of charge is less than or equal to 60%.
Use Table 2.4.3.2

## Slide 20: Table 2.4.3.2

## Slide 21: Finished Product Storage
Ceiling Height
Storage Height
Storage Arrangement
Packaging
State of Charge

## Slide 22
Finished Product – Solid Pile & Palletized

## Slide 23: Finished Product – Solid Pile & Palletized
45ft
(13.5m)

## Slide 24: Finished Product in Open Racks

## Slide 25: FMDS 7-112 Table 2.4.5.1.2

## Slide 26: Scenario 1

## Slide 27: Scenario 2

## Slide 28: Scenario 3

## Slide 29: Scenario 4

## Slide 30: Scenario 5

## Slide 31: Scenario 6

## Slide 32: Single-Row Rack Storage

## Slide 33: Double-Row Rack Storage

## Slide 34: Multi-Row Rack Storage

## Slide 35: Returned/Defective/Damaged
Isolate
Storage outside
Separate
Cut-off Rooms
500gpm hose stream
2-hour water supply for sprinkler and hose demand

## Slide 36: ASRS Protection
FMDS 8-34
Determine SOC
  <30%
  >30% <60%
  >60%

## Slide 37: A Continuing Challenge

## Slide 38: Current Status
Tests have been conducted at the module level to evaluate the performance of different fire suppressants such as water, wet chemical, and dry chemical. The tests concluded that water was the most effective fire suppressant.
Neither FM nor UL have any special tests or approvals for sprinklers protecting Lithium-ion cells or modules, but FM does provide specific guidance on how sprinkler systems are designed and supplied.
Sprinklers must be FM Approved and system design must meet all design requirements in FMDS 8-1 and 8-9 or related data sheets

## Slide 39: Learning Outcomes.
Discuss the hazards presented by Lithium-ion battery manufacturing and storage.
Navigate the current published protection guidance.
Identify the fire sprinklers that are approved to provide protection

## Slide 40
Contact —— .
James Lake
Director of Training IFSA
Email: jlake@ifsa.global
Phone: +1 617 372 6214
Web: www.ifsa.org